Emergency Responder Radio System

Coverage Report Test Results

| Date Prepared: | Apr 5, 2021 |
| --- | --- |
| Test File: | Seattle University CSI_20210405_101140 |
| Test Location: | Seattle University CSI |
|  | 901 12th Ave Seattle, WA 98122 |
| Technician: | Aaron Keyte |
| FCC#: | PG00066071 |

Building: Seattle University CSI

Result: Pass

Test Report Summary

| Channel/ Ch Group | Freq (MHz) | Technology | Band | Result | Area Points passed (%) | Critical Points passed (%) |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | 853.17500 | Custom Channel Power | Seattle Simulcast - PCC | Pass | 114/114 (100%) | 31/31 (100%) |

| Test Details |  |  |  |
| --- | --- | --- | --- |
| Number of Floors Tested: | 6 | Result Calculation: | By area per floor |
| Number of Areas Tested: | 114 | Area Pass Criteria: | 95% |
| Number of Critical Points Tested: | 31 | Critical Points Pass Criteria: | 99% |
|  |  | Apply Adjacent Area Rule: | No |

| Equipment Configuration |  |  |  |  |
| --- | --- | --- | --- | --- |
| Vendor | Application | Device | Calibration Expires | Antenna info |
| PCTEL | SeeHawk Touch rel 3.0.0.2 | SeeGull IBflex Device rel 3.5.0.0 SN: 081911044 | 11-13-2021 |  |

Threshold Settings

| Measurement | DL Area Point | UL Area Point | DL Critical Point | UL Critical Point | Use for grading |
| --- | --- | --- | --- | --- | --- |
| General Power (RSSI) | -95.0 dBm | -95.0 dBm | -95.0 dBm | -95.0 dBm | Yes |
| DAQ | 3.0 |  |  |  | No |

Floors Result

| Floor Plan | 1 853.17500 |
| --- | --- |
| Seattle U CSE - L6 | Pass |
| Seattle U CSE - L5 | Pass |
| Seattle U CSE - L4 | Pass |
| Seattle U CSE - L3 | Pass |
| Seattle U CSE - L2 | Pass |
| Seattle U CSE - L1 | Pass |

Floor: Seattle U CSE - L6

Channel: 1

Result: Pass

| Freq (MHz) | Tech | Band | Ant Gain | Cable Loss |  |  |  |  | Area Points passed (%) | Critical Points passed (%) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 853.17500 | Custom Channel Power | Seattle Simulcast - PCC | 0.00 | 0.00 |  |  |  |  | 14/14 (100%) | 3/3 (100%) |

| Grid | # of Areas | Area Size (sq. ft) | Area Width (ft) | Area Height (ft) | Comments |
| --- | --- | --- | --- | --- | --- |
| 1 | 20 | 612.63 | 20.53 | 29.85 |  |

Floor: Seattle U CSE - L6

Channel: 1

| Critical Point | DL Power (dBm) | DL DAQ | UL DAQ | Result | Comment |
| --- | --- | --- | --- | --- | --- |
| 1 | -78.19 | 5 | 5 | Pass | Stairwell |
| 2 | -77.27 | 5 | 5 | Pass | Stairwell |
| 3 | -72.20 | 5 | 5 | Pass | Elevator lobby |

| Grid | Area | DL Power (dBm) | DL DAQ | UL DAQ | Result | Comment |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | 1 | NT | NT | NT | NT |  |
| 1 | 2 | NT | NT | NT | NT |  |
| 1 | 3 | -54.78 | 5 | 5 | Pass |  |
| 1 | 4 | -45.69 | 5 | 5 | Pass |  |
| 1 | 5 | NT | NT | NT | NT |  |
| 1 | 6 | -75.55 | 5 | 5 | Pass |  |
| 1 | 7 | -63.93 | 5 | 5 | Pass |  |
| 1 | 8 | -54.06 | 5 | 5 | Pass |  |
| 1 | 9 | NT | NT | NT | NT |  |
| 1 | 10 | -72.79 | 5 | 5 | Pass |  |
| 1 | 11 | -70.93 | 5 | 5 | Pass |  |
| 1 | 12 | -72.56 | 5 | 5 | Pass |  |
| 1 | 13 | NT | NT | NT | NT |  |
| 1 | 14 | -71.49 | 5 | 5 | Pass |  |
| 1 | 15 | -71.07 | 5 | 5 | Pass |  |
| 1 | 16 | -67.80 | 5 | 5 | Pass |  |
| 1 | 17 | NT | NT | NT | NT |  |
| 1 | 18 | -77.06 | 5 | 5 | Pass |  |
| 1 | 19 | -62.20 | 5 | 5 | Pass |  |
| 1 | 20 | -70.77 | 5 | 5 | Pass |  |

Floor: Seattle U CSE - L5

Channel: 1

Result: Pass

| Freq (MHz) | Tech | Band | Ant Gain | Cable Loss |  |  |  |  | Area Points passed (%) | Critical Points passed (%) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 853.17500 | Custom Channel Power | Seattle Simulcast - PCC | 0.00 | 0.00 |  |  |  |  | 20/20 (100%) | 4/4 (100%) |

| Grid | # of Areas | Area Size (sq. ft) | Area Width (ft) | Area Height (ft) | Comments |
| --- | --- | --- | --- | --- | --- |
| 1 | 20 | 631.34 | 21.04 | 30.01 |  |

Floor: Seattle U CSE - L5

Channel: 1

| Critical Point | DL Power (dBm) | DL DAQ | UL DAQ | Result | Comment |
| --- | --- | --- | --- | --- | --- |
| 1 | -80.22 | 5 | 5 | Pass | Stairwell |
| 2 | -73.28 | 5 | 5 | Pass | Elevator lobby |
| 3 | -58.56 | 5 | 5 | Pass | Stairwell |
| 4 | -89.59 | 5 | 5 | Pass | Stairwell |

| Grid | Area | DL Power (dBm) | DL DAQ | UL DAQ | Result | Comment |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | 1 | -67.50 | 5 | 5 | Pass |  |
| 1 | 2 | -73.78 | 5 | 5 | Pass |  |
| 1 | 3 | -61.27 | 5 | 5 | Pass |  |
| 1 | 4 | -75.55 | 5 | 5 | Pass |  |
| 1 | 5 | -64.84 | 5 | 5 | Pass |  |
| 1 | 6 | -73.59 | 5 | 5 | Pass |  |
| 1 | 7 | -72.31 | 5 | 5 | Pass |  |
| 1 | 8 | -79.33 | 5 | 5 | Pass |  |
| 1 | 9 | -72.70 | 5 | 5 | Pass |  |
| 1 | 10 | -66.51 | 5 | 5 | Pass |  |
| 1 | 11 | -83.87 | 5 | 5 | Pass |  |
| 1 | 12 | -77.37 | 5 | 5 | Pass |  |
| 1 | 13 | -64.96 | 5 | 5 | Pass |  |
| 1 | 14 | -74.42 | 5 | 5 | Pass |  |
| 1 | 15 | -72.94 | 5 | 5 | Pass |  |
| 1 | 16 | -81.19 | 5 | 5 | Pass |  |
| 1 | 17 | -72.92 | 5 | 5 | Pass |  |
| 1 | 18 | -74.56 | 5 | 5 | Pass |  |
| 1 | 19 | -67.16 | 5 | 5 | Pass |  |
| 1 | 20 | -75.47 | 5 | 5 | Pass |  |

Floor: Seattle U CSE - L4

Channel: 1

Result: Pass

| Freq (MHz) | Tech | Band | Ant Gain | Cable Loss |  |  |  |  | Area Points passed (%) | Critical Points passed (%) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 853.17500 | Custom Channel Power | Seattle Simulcast - PCC | 0.00 | 0.00 |  |  |  |  | 20/20 (100%) | 4/4 (100%) |

| Grid | # of Areas | Area Size (sq. ft) | Area Width (ft) | Area Height (ft) | Comments |
| --- | --- | --- | --- | --- | --- |
| 1 | 20 | 649.68 | 21.48 | 30.25 |  |

Floor: Seattle U CSE - L4

Channel: 1

| Critical Point | DL Power (dBm) | DL DAQ | UL DAQ | Result | Comment |
| --- | --- | --- | --- | --- | --- |
| 1 | -52.99 | 5 | 5 | Pass | Stairwell |
| 2 | -77.68 | 5 | 5 | Pass | Stairwell |
| 3 | -53.08 | 5 | 5 | Pass | Stairwell |
| 4 | -66.66 | 5 | 5 | Pass | Elevator lobby |

| Grid | Area | DL Power (dBm) | DL DAQ | UL DAQ | Result | Comment |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | 1 | -65.55 | 5 | 5 | Pass |  |
| 1 | 2 | -53.83 | 5 | 5 | Pass |  |
| 1 | 3 | -69.13 | 5 | 5 | Pass |  |
| 1 | 4 | -63.61 | 5 | 5 | Pass |  |
| 1 | 5 | -73.81 | 5 | 5 | Pass |  |
| 1 | 6 | -56.56 | 5 | 5 | Pass |  |
| 1 | 7 | -63.29 | 5 | 5 | Pass |  |
| 1 | 8 | -65.59 | 5 | 5 | Pass |  |
| 1 | 9 | -54.65 | 5 | 5 | Pass |  |
| 1 | 10 | -59.25 | 5 | 5 | Pass |  |
| 1 | 11 | -59.06 | 5 | 5 | Pass |  |
| 1 | 12 | -68.61 | 5 | 5 | Pass |  |
| 1 | 13 | -62.07 | 5 | 5 | Pass |  |
| 1 | 14 | -67.80 | 5 | 5 | Pass |  |
| 1 | 15 | -67.92 | 5 | 5 | Pass |  |
| 1 | 16 | -77.83 | 5 | 5 | Pass |  |
| 1 | 17 | -63.36 | 5 | 5 | Pass |  |
| 1 | 18 | -64.36 | 5 | 5 | Pass |  |
| 1 | 19 | -52.26 | 5 | 5 | Pass |  |
| 1 | 20 | -61.79 | 5 | 5 | Pass |  |

Floor: Seattle U CSE - L3

Channel: 1

Result: Pass

| Freq (MHz) | Tech | Band | Ant Gain | Cable Loss |  |  |  |  | Area Points passed (%) | Critical Points passed (%) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 853.17500 | Custom Channel Power | Seattle Simulcast - PCC | 0.00 | 0.00 |  |  |  |  | 20/20 (100%) | 4/4 (100%) |

| Grid | # of Areas | Area Size (sq. ft) | Area Width (ft) | Area Height (ft) | Comments |
| --- | --- | --- | --- | --- | --- |
| 1 | 20 | 631.58 | 21.16 | 29.85 |  |

Floor: Seattle U CSE - L3

Channel: 1

| Critical Point | DL Power (dBm) | DL DAQ | UL DAQ | Result | Comment |
| --- | --- | --- | --- | --- | --- |
| 1 | -66.71 | 5 | 5 | Pass | Stairwell |
| 2 | -66.88 | 5 | 5 | Pass | Elevator lobby |
| 3 | -54.59 | 5 | 5 | Pass | Stairwell |
| 4 | -73.61 | 5 | 5 | Pass | Stairwell |

| Grid | Area | DL Power (dBm) | DL DAQ | UL DAQ | Result | Comment |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | 1 | -72.15 | 5 | 5 | Pass |  |
| 1 | 2 | -57.62 | 5 | 5 | Pass |  |
| 1 | 3 | -65.19 | 5 | 5 | Pass |  |
| 1 | 4 | -68.61 | 5 | 5 | Pass |  |
| 1 | 5 | -55.90 | 5 | 5 | Pass |  |
| 1 | 6 | -61.25 | 5 | 5 | Pass |  |
| 1 | 7 | -65.16 | 5 | 5 | Pass |  |
| 1 | 8 | -78.43 | 5 | 5 | Pass |  |
| 1 | 9 | -48.58 | 5 | 5 | Pass |  |
| 1 | 10 | -58.96 | 5 | 5 | Pass |  |
| 1 | 11 | -66.46 | 5 | 5 | Pass |  |
| 1 | 12 | -72.29 | 5 | 5 | Pass |  |
| 1 | 13 | -63.02 | 5 | 5 | Pass |  |
| 1 | 14 | -69.12 | 5 | 5 | Pass |  |
| 1 | 15 | -68.19 | 5 | 5 | Pass |  |
| 1 | 16 | -76.35 | 5 | 5 | Pass |  |
| 1 | 17 | -63.05 | 5 | 5 | Pass |  |
| 1 | 18 | -64.01 | 5 | 5 | Pass |  |
| 1 | 19 | -52.46 | 5 | 5 | Pass |  |
| 1 | 20 | -75.30 | 5 | 5 | Pass |  |

Floor: Seattle U CSE - L2

Channel: 1

Result: Pass

| Freq (MHz) | Tech | Band | Ant Gain | Cable Loss |  |  |  |  | Area Points passed (%) | Critical Points passed (%) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 853.17500 | Custom Channel Power | Seattle Simulcast - PCC | 0.00 | 0.00 |  |  |  |  | 20/20 (100%) | 5/5 (100%) |

| Grid | # of Areas | Area Size (sq. ft) | Area Width (ft) | Area Height (ft) | Comments |
| --- | --- | --- | --- | --- | --- |
| 1 | 20 | 620.52 | 21.38 | 29.02 |  |

Floor: Seattle U CSE - L2

Channel: 1

| Critical Point | DL Power (dBm) | DL DAQ | UL DAQ | Result | Comment |
| --- | --- | --- | --- | --- | --- |
| 1 | -55.89 | 5 | 5 | Pass | Stairwell |
| 2 | -64.66 | 5 | 5 | Pass | Stairwell |
| 3 | -62.03 | 5 | 5 | Pass | Stairwell |
| 4 | -70.02 | 5 | 5 | Pass | Elevator lobby |
| 5 | -69.89 | 5 | 5 | Pass | Stairwell |

| Grid | Area | DL Power (dBm) | DL DAQ | UL DAQ | Result | Comment |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | 1 | -64.42 | 5 | 5 | Pass |  |
| 1 | 2 | -61.56 | 5 | 5 | Pass |  |
| 1 | 3 | -50.31 | 5 | 5 | Pass |  |
| 1 | 4 | -56.80 | 5 | 5 | Pass |  |
| 1 | 5 | -62.72 | 5 | 5 | Pass |  |
| 1 | 6 | -65.12 | 5 | 5 | Pass |  |
| 1 | 7 | -62.03 | 5 | 5 | Pass |  |
| 1 | 8 | -71.58 | 5 | 5 | Pass |  |
| 1 | 9 | -56.27 | 5 | 5 | Pass |  |
| 1 | 10 | -64.83 | 5 | 5 | Pass |  |
| 1 | 11 | -55.41 | 5 | 5 | Pass |  |
| 1 | 12 | -74.32 | 5 | 5 | Pass |  |
| 1 | 13 | -69.20 | 5 | 5 | Pass |  |
| 1 | 14 | -67.87 | 5 | 5 | Pass |  |
| 1 | 15 | -64.88 | 5 | 5 | Pass |  |
| 1 | 16 | -76.31 | 5 | 5 | Pass |  |
| 1 | 17 | -62.04 | 5 | 5 | Pass |  |
| 1 | 18 | -67.14 | 5 | 5 | Pass |  |
| 1 | 19 | -40.98 | 5 | 5 | Pass |  |
| 1 | 20 | -55.08 | 5 | 5 | Pass |  |

Floor: Seattle U CSE - L1

Channel: 1

Result: Pass

| Freq (MHz) | Tech | Band | Ant Gain | Cable Loss |  |  |  |  | Area Points passed (%) | Critical Points passed (%) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 853.17500 | Custom Channel Power | Seattle Simulcast - PCC | 0.00 | 0.00 |  |  |  |  | 20/20 (100%) | 11/11 (100%) |

| Grid | # of Areas | Area Size (sq. ft) | Area Width (ft) | Area Height (ft) | Comments |
| --- | --- | --- | --- | --- | --- |
| 1 | 20 | 732.62 | 23.58 | 31.08 |  |

Floor: Seattle U CSE - L1

Channel: 1

| Reference Point Report |  |  |  |
| --- | --- | --- | --- |
| Reference Point | Power (dBm) | Selected | Comment |
| 1 | -53.25 |  | Outdoor |
| 2 | -64.78 |  | Outdoor |

| Critical Point | DL Power (dBm) | DL DAQ | UL DAQ | Result | Comment |
| --- | --- | --- | --- | --- | --- |
| 1 | -71.72 | 5 | 5 | Pass | Outdoor |
| 2 | -62.82 | 5 | 5 | Pass | Outdoor |
| 3 | -71.00 | 5 | 5 | Pass | Elevator lobby |
| 4 | -60.78 | 5 | 5 | Pass | Entrance |
| 5 | -71.23 | 5 | 5 | Pass | Entrance |
| 6 | -60.91 | 5 | 5 | Pass | Entrance |
| 7 | -67.13 | 5 | 5 | Pass | Outdoor |
| 8 | -71.28 | 5 | 5 | Pass | Entrance |
| 9 | -46.85 | 5 | 5 | Pass | Entrance |
| 10 | -54.39 | 5 | 5 | Pass | Entrance |
| 11 | -64.76 | 5 | 5 | Pass | Entrance |

| Grid | Area | DL Power (dBm) | DL DAQ | UL DAQ | Result | Comment |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | 1 | -65.17 | 5 | 5 | Pass |  |
| 1 | 2 | -59.66 | 5 | 5 | Pass |  |
| 1 | 3 | -47.04 | 5 | 5 | Pass |  |
| 1 | 4 | -61.68 | 5 | 5 | Pass |  |
| 1 | 5 | -65.10 | 5 | 5 | Pass |  |
| 1 | 6 | -59.22 | 5 | 5 | Pass |  |
| 1 | 7 | -48.53 | 5 | 5 | Pass |  |
| 1 | 8 | -72.41 | 5 | 5 | Pass |  |
| 1 | 9 | -60.62 | 5 | 5 | Pass |  |
| 1 | 10 | -63.93 | 5 | 5 | Pass |  |
| 1 | 11 | -58.65 | 5 | 5 | Pass |  |
| 1 | 12 | -64.61 | 5 | 5 | Pass |  |
| 1 | 13 | -53.63 | 5 | 5 | Pass |  |
| 1 | 14 | -74.76 | 5 | 5 | Pass |  |
| 1 | 15 | -53.82 | 5 | 5 | Pass |  |
| 1 | 16 | -68.51 | 5 | 5 | Pass |  |
| 1 | 17 | -43.59 | 5 | 5 | Pass |  |
| 1 | 18 | -48.83 | 5 | 5 | Pass |  |
| 1 | 19 | -69.84 | 5 | 5 | Pass |  |
| 1 | 20 | -70.78 | 5 | 5 | Pass |  |